## Slide 1
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
VLF E Series VLF and Tan Delta Hook Up and control with E-Link

## Slide 2: Disclaimer
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
This guide for the High Voltage, Inc. E Series of VLF hipot and Tan Delta bridge hook up is meant to be for reference only. The instructions are intended to be clear and simple, but the operator must be trained and qualified according to the customer’s established procedures for the use of this type of equipment.

## Slide 3: VLF and Tan Delta Hook Up
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA

## Slide 4: Step 1: Ground VLF and Tan Delta Bridge Connect the ground stud of the VLF and Tan Delta Bridge to the grounded concentric neutral of the cable under test
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
Grounded
Neutral
VLF-34E Shown
TD-65E Shown

## Slide 5: Step 2: Install High Voltage Output Cable from VLF to Tan Delta Bridge
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
MC Connector, Push in to install
Push in, then pull out to remove
Push in MC Connector into socket
and pigtail ground to ground stud
Install shielded output cable
supplied with TD Bridge

## Slide 6: Step 3: Install High Voltage Output Cable from Tan Delta Bridge to cable under test
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
White insulated, unshielded output
cable plugs into sphere and clip goes to
cable under test. Keep this cable away
from ground 6-8 inches (12cm – 20cm)
or more. Use the supplied corona suppressing
toroid to reduce electrical discharge (PD)

## Slide 7: Step 4: Power on VLF and Tan Delta Bridge
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
Turn on both the VLF
And Tan Delta Bridge
Light should blink
green, if red change
the batteries

## Slide 8: Step 5: Set VLF Measurement Source to TD
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
Push the blue button to enter Advanced screen
Scroll down to “Measurement Source”
Push down on the encoder or press the green button
Choose TD-34/65, TD-34, or TD-65 (depending on model)
Push down on the encoder or press the green button
Check light on Tan Delta module

## Slide 9: Step 6: Verify solid green light on Tan Delta bridge
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
The light on the Tan Delta Bridge should change
from blinking green to solid green confirming the
Xbee wireless connection between the VLF and Tan
Delta bridge has been established

## Slide 10: Step 7: The VLF and Tan Delta are ready to test
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
Press the blue button for “New Test Setup”
Choose “Sinewave “ for waveform
Choose the desired output frequency (0.1Hz)
Choose voltage step 1
  Set up first test voltage (0.5 x u0)
  Set duration for 3 minutes
Choose voltage step 2
  Set up first test voltage (u0)
  Set duration for 3 minutes
Choose voltage step 3
  Set up first test voltage (1.5 x u0)
  Set duration for 3 minutes
Choose “Fault” as “Overload on Arc”
Press the blue button to start the test

## Slide 11: Control of VLF and Tan Delta via E-Link with PC
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA

## Slide 12: Step 8: Insert the green USB Xbee Antenna into PC
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
Plug green USB Xbee Antenna into PC
Install the drivers for the Xbee Antenna
Download via the Internet (or)
Download via the red HVI flash drive

## Slide 13: Step 9: Open E-Link Software
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
Install the E-Link software from the red HVI flash drive
Open the E-Link software
Click on “Settings”
Click on the “Communications” tab
Click the “Auto Detect” button
The software should automatically assign a serial port
Click “Close”
If you have issues please contact factory@hvinc.com

## Slide 14: Step 10: Click “RUN TEST”
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA

## Slide 15: Step 11: Ready to program the test using E-Link
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
Choose “VLF/TD” as your “Measurement Source”
Choose “Sinewave” as your “Waveform”
Choose your output frequency (.1Hz is normal for TD)
Choose voltage step 1
  Set up first test voltage (0.5 x u0)
  Set duration for 3 minutes
Choose voltage step 2
  Set up first test voltage (u0)
  Set duration for 3 minutes
Choose voltage step 3
  Set up first test voltage (1.5 x u0)
  Set duration for 3 minutes
Choose “Fault” as “Overload on Arc”
Click the green “Start” Button

## Slide 16
ISO 9001 2008
The World’s Source for High Voltage Test Equipment
MADE IN THE USA
High Voltage, Inc. • hvinc.com • p. 518.329.3275 • f. 518.329.3271 • 31 County Route 7A • Copake, NY 12516 USA
Thank you for watching, if you have any questions please contact
High Voltage, Inc. or your local High Voltage, Inc. sales representative
Thank You
from